## Sheet1
LV Transformer 001
Building Number
Phase
Foreman: | Equip ID:
Equipment Information: |  | Date | Int. | Notes
RIF Completed
Labels installed by QCX:
Phenolic
Arc Flash
QCX
Equipment Mounted / Installation Specs
6" clearance from walls and panels
Remove front cover bolts, bag & tag, leaving proper amount of bolts to hold cover in place
Shipping assembly (if required)
Apply proper cover for equipment protection
Anchored using 1/2" concrete wedge anchors
Housing is mounted squared and leveled
XFMR Neta Tested (validated by QCx)
QCX Handoff to Construction
Internal Wiring and Termination Specifications
1. Hardware Installation:
Install proper/correct phase lugs (with min 1" gap from nearest item)
Install proper ground bar (if required)
2. Primary / High Side:
Primary wire matches 1 Line Diagram: (3) AL #1/0 and 1 CU #6 Ground (A100.3)
Verify primary wire phase color: H1/A-Brown H2/B-Orange H3/C-Yellow Ground-Green
Verify installation and termination of ground bonding bushing
3. Secondary / Low Side:
Secondary wire matches 1 Line Diagram: (3) AL # 1/0 and Ground 1 CU #6 (A100.3) Neutral wire AL # 1/0 (A110.T)
Verify secondary wire phase color: X1/A-Black X2/B-Red X3/C-Blue Ground-Green Neutral-White
Verify installation and termination of ground bonding bushing
4. Building Steel:
Verify that ground is #8 copper or larger
5. Bonding Jumper:
Bonding jumper must be AL # 1/0 wire (or same size as biggest conducter on pri. or sec.) and all black
6. Verify hardware kit matches attached inventory sheet
7. Install front cover with all hardware
Foreman in charge verify all complete and handoff to QCX
Construction Foreman Name:
QCX Foreman Name:
Date:

## Scans
scannedAtLocalISO | scannedAtLocalText | code | valid | deviceId | method | userAgent
2025-12-23T21:30:00.088Z |  | 1090642 | TRUE | c3086ca0-e646-4ecb-9784-7958eb1c297b | qr
2025-12-23T21:30:01.036Z |  | 1090642 | TRUE | c3086ca0-e646-4ecb-9784-7958eb1c297b | qr
2025-12-23T21:30:01.969Z |  | 1090642 | TRUE | c3086ca0-e646-4ecb-9784-7958eb1c297b | qr
2025-12-29T13:32:01.166Z |  | 1090642 | TRUE | c3086ca0-e646-4ecb-9784-7958eb1c297b | qr
2025-12-29T13:32:02.099Z |  | 1090642 | TRUE | c3086ca0-e646-4ecb-9784-7958eb1c297b | qr
2025-12-29T15:14:26.708Z |  | 1090642 | TRUE | c3086ca0-e646-4ecb-9784-7958eb1c297b | qr
2025-12-29T18:18:48.814Z |  | 1090642 | TRUE | c3086ca0-e646-4ecb-9784-7958eb1c297b | qr
2025-12-29T18:18:49.997Z |  | 1090642 | TRUE | c3086ca0-e646-4ecb-9784-7958eb1c297b | qr
2025-12-30T15:16:36.725Z |  | 1090642 | TRUE | c3086ca0-e646-4ecb-9784-7958eb1c297b | manual
2025-12-30T16:19:44.512Z |  | 1090642 | TRUE | c3086ca0-e646-4ecb-9784-7958eb1c297b | manual
2026-01-07T16:04:58.622Z |  | 1090642 | TRUE | c3086ca0-e646-4ecb-9784-7958eb1c297b | qr
2026-01-07T16:27:25.390Z |  | 1090733 | TRUE | c3086ca0-e646-4ecb-9784-7958eb1c297b | qr
2026-01-13T16:54:03.430Z |  | 1090033 | TRUE | ee3ae54c-bcd4-4361-bdeb-4b610229b08e | manual
2026-01-13T16:54:06.325Z |  | 1090033 | TRUE | ee3ae54c-bcd4-4361-bdeb-4b610229b08e | manual
2026-01-13T16:58:01.800Z |  | 1090033 | TRUE | ee3ae54c-bcd4-4361-bdeb-4b610229b08e | manual
2026-01-13T16:58:06.262Z |  | 1090033 | TRUE | ee3ae54c-bcd4-4361-bdeb-4b610229b08e | manual
2026-01-13T16:58:08.077Z |  | 1090033 | TRUE | ee3ae54c-bcd4-4361-bdeb-4b610229b08e | manual
2026-01-13T17:19:17.102Z |  | 1090033 | TRUE | ee3ae54c-bcd4-4361-bdeb-4b610229b08e | manual
2026-01-13T19:02:30.527Z |  | 1090033 | TRUE | ee3ae54c-bcd4-4361-bdeb-4b610229b08e | manual
2026-01-14T13:33:00.989Z |  | 1090642 | TRUE | c3086ca0-e646-4ecb-9784-7958eb1c297b | qr
2026-01-14T13:45:34.796Z |  | 1090733 | TRUE | cdb71622-f5e3-4b91-baf3-4de9b1f25292 | qr
2026-01-14T13:45:35.802Z |  | 1090733 | TRUE | cdb71622-f5e3-4b91-baf3-4de9b1f25292 | qr
2026-01-14T15:27:29.205Z |  | 1090642 | TRUE | 99a99233-fd2f-44f8-97c5-55d279ef253b | qr
2026-01-14T15:27:30.254Z |  | 1090642 | TRUE | 99a99233-fd2f-44f8-97c5-55d279ef253b | qr
2026-01-14T15:27:31.187Z |  | 1090642 | TRUE | 99a99233-fd2f-44f8-97c5-55d279ef253b | qr
2026-01-14T15:27:32.120Z |  | 1090642 | TRUE | 99a99233-fd2f-44f8-97c5-55d279ef253b | qr
2026-01-14T15:38:58.495Z |  | 1090642 | TRUE | 99a99233-fd2f-44f8-97c5-55d279ef253b | qr
2026-01-14T15:38:59.427Z |  | 1090642 | TRUE | 99a99233-fd2f-44f8-97c5-55d279ef253b | qr
2026-01-14T15:39:01.369Z |  | 1090642 | TRUE | 99a99233-fd2f-44f8-97c5-55d279ef253b | qr
2026-01-14T18:56:09.367Z |  | 1090033 | TRUE | ee3ae54c-bcd4-4361-bdeb-4b610229b08e | manual
2026-01-14T18:56:12.390Z |  | 1090033 | TRUE | ee3ae54c-bcd4-4361-bdeb-4b610229b08e | manual
2026-01-15T16:19:37.037Z |  | 1090733 | TRUE | 99a99233-fd2f-44f8-97c5-55d279ef253b | qr
2026-01-15T16:19:38.263Z |  | 1090733 | TRUE | 99a99233-fd2f-44f8-97c5-55d279ef253b | qr